## Cooling Load
COOLING LOAD CALCULATION
PROJECT: HBE_HANUMAN BREWERY EXTENSION | [14 empty] | DATE | : 27 Oct 2026
LOCATION : FINISH GOOD WAREHOUSE BUILDING , ST. 2004, SANGKAT O BEK KAM, KHAN SEN SOK, PHNOM PENH, CAMBODIA | [14 empty] | REV. | : 0
PREPARED BY: ANNE HERLIANA | [14 empty] | CHECKED BY | : JAIME QUILALA
NO. | ROOM NO | LEVEL | ROOM NAME | AREA (M²) | CALCULATION AS PER HAP SOFTWARE |  |  |  |  | SELECTION EQUIPMENT DAIKIN | [6 empty] | REMARK
[5 empty] | DESIGN TEMP. (°C) | SENSIBLE LOAD (KW) | LATENT LOAD (KW) | TOTAL LOAD (KW) | AIRFLOW (CMH) | TAG NO | TYPE | MODEL | TOTAL LOAD (KW) | QTY | POWER SUPPLY VOLTAGE - PHASE | POWER CONSUMPTION (kW)
1 | D-001 | Finish Good Warehouse -GF | TAX OFF | 26 | 24±2 | 3.1 | 1.1 |  | 1015.2 | IU/OU D-001 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 5.28 | 1 | 220V-240V / 50 HZ | 0.89
2 | D-002 | Finish Good Warehouse -GF | DRIVER RM | 48 | 24±2 | 5.6 | 2.9 |  | 1702.8 | IU/OU D-002 | CEILING CASSETTE | FCF100CVM/RZF100CYM | 10 | 1 | 3 PHASE , 380-415 V, 50 HZ | 2.97
3 | D-008 | Finish Good Warehouse -GF | LOGISTIS OFF. MANAGER | 10 | 24±2 | 0.9 | 0.5 |  | 277.2 | IU/OU D-003 | WALL MOUNTED | FTKE25AV1F/RKE25AV1 | 2.64 | 1 | 220V-240V / 50 HZ | 0.89
4 | D-009 | Finish Good Warehouse -GF | LOGISTIS OFF. | 42 | 24±2 | 4 | 1.1 |  | 1310.4 | IU/OU D-004 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 5.6 | 1 | 220V-240V / 50 HZ | 2
5 | D-010 | Finish Good Warehouse -GF | WAREHOUSE COUNTER OFF. | 48 | 24±2 | 6.8 | 2 |  | 2239.2 | IU/OU D-005 | CEILING CASSETTE | FCF100CVM/RZF100CYM | 10 | 1 | 3 PHASE , 380-415 V, 50 HZ | 2.97
6 | D-011 | Finish Good Warehouse -GF | SUPERVISOR | 15 | 24±2 | 2.3 | 0.6 |  | 777.6 | IU/OU D-006 | WALL MOUNTED | FTKE35AV1F/RKE35AV1 | 3.6 | 1 | 220V-240V / 50 HZ | 1
7 | D-017 | Finish Good Warehouse -GF | ELECTRICAL ROOM | 4 | 22±2 | 2 | 0.2 |  | 986.4 | IU/OU D-007 | WALL MOUNTED | FTKE25AV1F/RKE25AV1 | 2.64 | 1 | 220V-240V / 50 HZ | 0.89
8 | D-101 | Finish Good Warehouse -1F | MEETING ROOM | 57 | 24±2 | 6.9 | 4.3 |  | 2088 | IU/OU D-101 | CEILING CASSETTE | FCF125CVM/RZF125CYM | 12.5 | 1 | 3 PHASE , 380-415 V, 50 HZ | 4.18
9 | D-102 | Finish Good Warehouse -1F | PANTRY | 33 | 24±2 | 4.3 | 2.1 |  | 1317.6 | IU/OU D-102 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 9 | 1 | 220V-240V / 50 HZ | 2
10 | D-107 | Finish Good Warehouse -1F | SUPERVISOR OFFICE 1 | 15 | 24±2 | 4 | 0.6 |  | 1389.6 | IU/OU D-105 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 4.5 | 1 | 220V-240V / 50 HZ | 2
11 | D-108 | Finish Good Warehouse -1F | SUPERVISOR OFFICE 2 | 14 | 24±2 | 3.6 | 0.5 |  | 1270.8 | IU/OU D-106 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 4.5 | 1 | 220V-240V / 50 HZ | 2
12 | D-106 | Finish Good Warehouse -1F | OFFICE | 36 | 24±2 | 4.5 | 1.7 |  | 1400.4 | IU/OU D-107 | WALL MOUNTED | FTKE60AV1F/RKE60AV1 | 7.1 | 1 | 220V-240V / 50 HZ | 2
13 | D-109 | Finish Good Warehouse -1F | MANAGER OFFICE 1 | 15 | 24±2 | 3.6 | 0.6 |  | 1288.8 | IU/OU D-108 | WALL MOUNTED | FTKE50AV1F/RKE50AV1 | 4.5 | 1 | 220V-240V / 50 HZ | 2
14 | D-110 | Finish Good Warehouse -1F | MANAGER OFFICE 2 | 17 | 24±2 | 1.6 | 0.6 |  | 511.2 | IU/OU D-109 | WALL MOUNTED | FTKE25AV1F/RKE25AV1 | 2.64 | 1 | 220V-240V / 50 HZ | 0.89

## Fan Schedule
FAN EQUIPMENT SCHEDULE
FINISH GOOD WAREHOUSE
TAG NO | ROOM NO | ROOM NAME | TYPE/MODEL | AIR FLOW TOTAL CMH | EXTERNAL STATIC PRESSURE PASCAL | NOMINAL DATA *) |  |  |  | ELECTRICAL |  | QTY | NOTE
[6 empty] | BLADE DIAMETER MM | Speed RPM | WEIGHT KG | Max. Noise Level dbA @ 3m | Estimated Fan Motor Power KW | (V / PH / HZ)
EF D-001.01~45 |  | FINISH GOOD WAREHOUSE | WALL MOUNTED - INDUSTRIAL TYPE | 27970 | 50 | 775 | 1425 | 72 | 84 | 3.7 | 380-415 V/ 50 HZ | 45
EF D-002 |  | SUGAR STORAGE | WALL MOUNTED - INDUSTRIAL TYPE | 18220 | 50 | 775 | 1425 | 52 | 81 | 1.1 | 380-415 V/ 50 HZ | 1
EF D-003 |  | DRIVER TOILET | INLINE CENTRIFUGAL CABINET FAN | 410 | 100 | 302 | 1334 | 14 | 50 | 0.07 | 220V-240V / 50 HZ | 1
EF D-004 |  | MALE TOILET FEMALE TOILET JANITOR | INLINE CENTRIFUGAL CABINET FAN | 650 | 100 | 302 | 1486 | 14 | 53 | 0.07 | 220V-240V / 50 HZ | 1
EF D-101 |  | LOCKER | CEILING MOUNTED SIROCCO VENTILATING FANS | 520 | 80 |  | 1169 | 11 | 44 | 0.05 | 220V-240V / 50 HZ | 1
EF D-102 |  | ARCHIEVE ROOM | CEILING MOUNTED SIROCCO VENTILATING FANS | 630 | 80 |  | 1047 | 14 | 50 | 0.07 | 220V-240V / 50 HZ | 1
EF D-103 |  | PANTRY | CEILING MOUNTED SIROCCO VENTILATING FANS | 590 | 80 |  | 1353 | 11 | 49 | 0.08 | 220V-240V / 50 HZ | 1
CF D-101 |  | LOCKER | CEILING PROPELLER 5 SPEED CONTROL | 12780 |  | DIA 1500 MM |  | 6.2 |  | 0.07 | 1/220/50 | 1
CF D-102 |  | ARCHIEVE ROOM | CEILING PROPELLER 5 SPEED CONTROL | 12780 |  | DIA 1500 MM |  | 6.2 |  | 0.07 | 1/220/50 | 1
NOTES – FAN EQUIPMENT SCHEDULE (DETAIL DESIGN)
1. THE EQUIPMENT SCHEDULE INDICATED ON THE DRAWINGS SPECIFIES THE REQUIRED CAPACITY, FUNCTIONAL PERFORMANCE, AND TECHNICAL PARAMETERS FOR THE FINAL PROCUREMENT AND INSTALLATION.
2. THE CONTRACTOR SHALL VERIFY ALL SITE CONDITIONS, PHYSICAL SPACE LIMITATIONS, ACTUAL SYSTEM LAYOUTS, AND TOTAL PRESSURE DROPS PRIOR TO ORDERING ANY FAN EQUIPMENT.
3. FAN PERFORMANCE SHALL BE CERTIFIED BY AMCA (OR EQUIVALENT STANDARDS) TO OPERATE AT THE OPTIMUM EFFICIENCY POINT WHILE MEETING THE REQUIRED AIRFLOW, ACTUAL STATIC PRESSURE, AND PROJECT ACUSTIC/NOISE CRITERIA.
4. FAN MOTORS SHALL BE HIGH-EFFICIENCY, TEFC TYPE, SUITABLE FOR CONTINUOUS OPERATION AND MATCHING THE PROVISIONED PROJEC ELECTRICAL VOLTAGE, PHASE, AND CONTROLS.
5. VARIABLE SPEED DRIVES (VSDs) OR INVERTERS SHALL BE PROVIDED WHERE INDICATED FOR AIRFLOW BALANCING, AUTOMATED SYSTEM CONTROL, AND ENERGY-EFFICIENT OPERATION.
6. ALL FANS SHALL BE COMPLETE WITH APPROPRIATE VIBRATION ISOLATORS, FLEXIBLE DUCT CONNECTORS, BACKDRAFT DAMPERS, INTERNAL ACCESS DOORS, MOUNTING BRACKETS, AND INDEPENDENT STRUCTURAL SUPPORTS.
7. COORDINATE THE FINAL PHYSICAL INSTALLATION OF FANS WITH ARCHITECTURAL FINISHES, STRUCTURAL FRAMING, ELECTRICAL ROUTING, AND OTHER MEP SERVICES TO GUARANTEE ACCESSIBILITY FOR MAINTENANCE AND FILTER REPLACEMENT.
8. THE CONTRACTOR SHALL SUBMIT FINAL EQUIPMENT SELECTION DATA, CERTIFIED PERFORMANCE CURVES, SOUND SPECTRUM DATA, MOTOR DATA SHEETS, CONTROL DIAGRAMS, AND DETAILED SHOP DRAWINGS FOR CONSULTANT APPROVAL BEFORE FABRICATION.
9. ALL FANS SHALL BE RIGOROUSLY TESTED, COMMISSIONED, AND BALANCED. A COMPLETE TESTING, ADJUSTING, AND BALANCING (TAB) REPORT SHALL BE SUBMITTED TO ACHIEVE THE DESIGN DESIGNATED PARAMETERS.
10. UNLESS OTHERWISE NOTED, ALL AIRFLOW VALUES ARE EXPRESSED IN CMH (M³/H) AND EXTERNAL STATIC PRESSURE IN PA.