## CP-FGW-L0-MVAC
FINISH GOOD WAREHOUSE - MVAC
CP-FGW-L0-MVAC (IP 42) - GABUNGAN L0 + L1, SUPPLY FROM MDB-FGW-L0 (TIDAK LAGI DARI DEG)
BOX PANEL - LOCATION AT FINISH GOOD WAREHOUSE
380/220V, 3PH, 4W, 50Hz - cos phi 0.8
cos phi |  | 0.8
V (L-L) |  | 380
NO. | BREAKER | CABLE | FUNCTION | EQUIPMENT |  | DEMAND LOAD (WATT) |  |  | REMARKS | STARTER
|  |  |  | LOAD EQUIPMENT (WATT) | PHASE | R | S | T
1 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.01 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
2 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.02 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
3 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.03 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
4 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.04 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
5 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.05 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
6 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.06 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
7 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.07 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
8 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.08 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
9 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.09 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
10 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.10 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
11 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.11 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
12 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.12 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
13 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.13 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
14 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.14 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
15 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.15 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
16 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.16 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
17 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.17 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
18 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.18 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
19 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.19 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
20 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.20 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
21 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.21 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
22 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.22 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
23 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.23 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
24 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.24 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
25 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.25 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
26 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.26 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
27 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.27 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
28 | MCB-3P 16A 6kA | 1x3C-4mm2 (FRC) Cu/MGT/XLPE/LSZH +1C-4mm2 Cu/PVC G/Y | EF D-001.28 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR, CONNECT TO FIRE ALARM | DOL
29 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.29 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
30 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.30 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
31 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.31 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
32 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.32 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
33 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.33 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
34 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.34 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
35 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.35 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
36 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.36 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
37 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.37 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
38 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.38 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
39 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.39 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
40 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.40 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
41 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.41 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
42 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.42 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
43 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.43 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
44 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.44 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
45 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-001.45 WALL FAN FINISH GOOD WAREHOUSE (D-012) | 3700 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
46 | MCB-3P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC +1C-4mm2 Cu/PVC G/Y | EF D-002 SUGAR STORAGE | 1100 | 3 PH |  |  |  | WALL MOUNTED INDUSTRIAL FAN, NORMAL OPERATION, CONNECT TO FIRE ALARM | DOL
47 | MCB-3P 16A 6kA | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (N+E) | IU/OU D-002 DRIVER RM (D-002) | 2970 | 3 PH |  |  |  | CEILING CASSETTE, FCF100CVM/RZF100CYM | DOL
48 | MCB-3P 16A 6kA | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (N+E) | IU/OU D-005 WAREHOUSE COUNTER OFF. (D-010) | 2970 | 3 PH |  |  |  | CEILING CASSETTE, FCF100CVM/RZF100CYM | DOL
49 | MCB-3P 16A 6kA | 1x5C-4mm2 Cu/XLPE/PVC INCLUDING (N+E) | IU/OU D-101 MEETING ROOM (D-101) | 4180 | 3 PH |  |  |  | CEILING CASSETTE, FCF125CVM/RZF125CYM | DOL
50 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-001 TAX OFF (D-001) | 890 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
51 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-003 LOGISTIC OFF. MANAGER (D-008) | 890 | 1 PH |  |  |  | WALL MOUNTED, FTKE25AV1F/RKE25AV1 | DOL
52 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-004 LOGISTIC OFF. (D-009) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
53 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-006 SUPERVISOR (D-011) | 1000 | 1 PH |  |  |  | WALL MOUNTED, FTKE35AV1F/RKE35AV1 | DOL
54 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-007 ELECTRICAL ROOM (D-017) | 890 | 1 PH |  |  |  | WALL MOUNTED, FTKE25AV1F/RKE25AV1 | DOL
55 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-102 PANTRY (D-102) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
56 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-105 SUPERVISOR OFFICE 1 (D-107) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
57 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-106 SUPERVISOR OFFICE 2 (D-108) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
58 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-107 OFFICE (D-106) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE60AV1F/RKE60AV1 | DOL
59 | MCB-1P 16A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-108 MANAGER OFFICE 1 (D-109) | 2000 | 1 PH |  |  |  | WALL MOUNTED, FTKE50AV1F/RKE50AV1 | DOL
60 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | IU/OU D-109 MANAGER OFFICE 2 (D-110) | 890 | 1 PH |  |  |  | WALL MOUNTED, FTKE25AV1F/RKE25AV1 | DOL
61 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | EF D-003 DRIVER TOILET (D-003) | 70 | 1 PH |  |  |  | INLINE CENTRIFUGAL CABINET FAN | DOL
62 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | EF D-004 TOILET & JANITOR (D-005,006,007) | 70 | 1 PH |  |  |  | INLINE CENTRIFUGAL CABINET FAN | DOL
63 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | EF/CF D-101 LOCKER (D-103) | 120 | 1 PH |  |  |  | SIROCCO VENT. FAN 50W + CEILING PROPELLER FAN 70W | DOL
64 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | EF/CF D-102 ARCHIVE ROOM (D-105) | 140 | 1 PH |  |  |  | SIROCCO VENT. FAN 70W + CEILING PROPELLER FAN 70W | DOL
65 | MCB-1P 10A 6kA | 1x3C-4mm2 Cu/XLPE/PVC INCLUDING (E) | EF D-103 PANTRY (D-102) | 80 | 1 PH |  |  |  | CEILING MOUNTED SIROCCO VENTILATING FAN | DOL
66 |  |  | SPARE
67 |  |  | SPARE
68 |  |  | SPARE
SUB TOTAL
TOTAL WATT
TOTAL VA
CONNECTED AMPERE
DIVERSITY FACTOR Ku | [5 empty] | 0.9
SPARE | [5 empty] | 20%
Pact (kW) = TOTAL WATT x Ku x (1 + SPARE)
DESIGN AMPERE = Pact / (SQRT(3) x V x cos phi)
INCOMING (lihat catatan 5) | [5 empty] | MCCB-3P 500A
SUMBER DATA & RUMUS
1. Isi sheet ini mengikuti gambar ME-D-LV-6002 R2 (CP-FGW-L0-MVAC): 65 circuit + 3 spare. Beban dari HBE Cooling Load Calculation (Daikin split) & Fan Equipment Schedule FG Warehouse.
2. DEMAND LOAD R/S/T = beban circuit; circuit 3 fase dibagi rata 3 (=$E/3). Beban 1 fase mengikuti label fasa di gambar (diseimbangkan R/S/T).
3. SUB TOTAL = SUM per kolom fase; TOTAL WATT = R + S + T; TOTAL VA = TOTAL WATT / cos phi (C5); CONNECTED AMPERE = TOTAL VA / (SQRT(3) x V L-L) (C6).
4. STARTER: beban 5 kW ke atas memakai SOFT STARTER (SS) dengan bypass, di bawah 5 kW memakai DOL. R2: semua beban < 5 kW -> DOL (fan 3.7 kW).
5. Kabel motor 3 fase: 1x3C + 1C earthing. Fan 3.7 kW: FLA 7.0 A -> MCB-3P 16A, 3C-4mm2. AC 3 fase (RZF-CYM, 3N~): 1x5C-4mm2 incl. N+E, MCB-3P 16A. AC 1 fase: 3C-4mm2, 10A/16A.
Panjang kabel = ESTIMASI dari posisi tag di layout ME-D-SO-1102 (jarak siku + 12 m naik, x 1.1). Model Revit FGW belum dipakai - perlu dicek ke rute cable tray.
6. Incoming: MCCB-3P 500A 36kA dari MDB-FGW-L0, kabel 2x(1x4C-240mm2) + 1x(1C-120mm2 G/Y), CT 500/5A, busbar 630A. Lihat sheet CABLE SIZING. Breaker feeder di MDB-FGW-L0 perlu disesuaikan.
7. EF D-001.09~28 ACTIVE ON EMERGENCY (kabel FRC) + EF D-001.01~08 & 29~45 NORMAL, semua dengan kontaktor 24VDC interlock ke fire alarm. Status EF D-001.29~45 perlu dikonfirmasi.
8. Sesuai note 12 sheet FAN: BS EN 12101-3 F400/120, motor class H, kabel tahan api, emergency overload bypass - starter DOL fan smoke perlu bypass overload darurat.
9. Sel kuning (cos phi, tegangan, LOAD EQUIPMENT, Ku, spare) adalah input - boleh diubah.

## CP-FGW-L1-MVAC
FINISH GOOD WAREHOUSE - MVAC
CP-FGW-L1-MVAC (IP 42) - VOID: DIGABUNG KE CP-FGW-L0-MVAC, TIDAK LAGI DARI DEG
BOX PANEL - LOCATION AT FINISH GOOD WAREHOUSE
380/220V, 3PH, 4W, 50Hz - cos phi 0.8 - ALL CIRCUITS CONNECT TO FIRE ALARM
cos phi |  | 0.8
V (L-L) |  | 380
NO. | BREAKER | CABLE | FUNCTION | EQUIPMENT |  | DEMAND LOAD (WATT) |  |  | REMARKS
|  |  |  | LOAD EQUIPMENT (WATT) | PHASE | R | S | T
1 |  |  | EF D-001.09 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
2 |  |  | EF D-001.10 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
3 |  |  | EF D-001.11 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
4 |  |  | EF D-001.12 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
5 |  |  | EF D-001.13 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
6 |  |  | EF D-001.14 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
7 |  |  | EF D-001.15 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
8 |  |  | EF D-001.16 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
9 |  |  | EF D-001.17 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
10 |  |  | EF D-001.18 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
11 |  |  | EF D-001.19 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
12 |  |  | EF D-001.20 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
13 |  |  | EF D-001.21 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
14 |  |  | EF D-001.22 ROOF FAN SMOKE EXTRACTION (D-012) | 198900 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
15 |  |  | EF D-001.23 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
16 |  |  | EF D-001.24 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
17 |  |  | EF D-001.25 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
18 |  |  | EF D-001.26 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
19 |  |  | EF D-001.27 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
20 |  |  | EF D-001.28 ROOF FAN SMOKE EXTRACTION (D-012) | 19152 | 3 PH |  |  |  | ACTIVE ON EMERGENCY, F400/120, CLASS H MOTOR
21 |  |  | EF D-001.01 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
22 |  |  | EF D-001.02 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
23 |  |  | EF D-001.03 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
24 |  |  | EF D-001.04 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
25 |  |  | EF D-001.05 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
26 |  |  | EF D-001.06 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
27 |  |  | EF D-001.07 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
28 |  |  | EF D-001.08 ROOF FAN FINISH GOOD WAREHOUSE (D-012) | 19152 | 3 PH |  |  |  | NORMAL OPERATION, QEI-54-200
29 |  |  | SPARE
30 |  |  | SPARE
31 |  |  | SPARE
SUB TOTAL
TOTAL WATT
TOTAL VA
CONNECTED AMPERE
DIVERSITY FACTOR Ku | [5 empty] | 0.9
SPARE | [5 empty] | 20%
Pact (kW) = TOTAL WATT x Ku x (1 + SPARE) / 1000
DESIGN AMPERE = Pact / (SQRT(3) x V x cos phi)
INCOMING (lihat catatan 5) | [5 empty] | MCCB-3P 1250A
SUMBER DATA & RUMUS
1. Beban (kolom LOAD EQUIPMENT) diambil dari TD HVAC EQUIPMENT SCHEDULE FG WAREHOUSE (sheet FAN: ESTIMATED FAN MOTOR POWER).
2. DEMAND LOAD R/S/T = beban circuit; circuit 3 fase dibagi rata 3 (=$E/3). Beban 1 fase dirotasi R-S-T.
3. SUB TOTAL = SUM per kolom fase; TOTAL WATT = R + S + T; TOTAL VA = TOTAL WATT / cos phi (C5);
CONNECTED AMPERE = TOTAL VA / (SQRT(3) x V L-L) (C6).
4. Ukuran breaker & kabel: I = P / (SQRT(3) x 380 x 0.8), dikali 1.25 untuk circuit motor, dibulatkan
ke rating standar terdekat. ASUMSI PERENCANA - harap dicek terhadap data motor aktual dari vendor.
5. Incoming: MCCB-3P 1250A 36kA dari DEG, kabel 4x(1x4C-240mm² Cu/MGT/XLPE/LSZH (FRC)) + 2x(1C-120mm² G/Y), CT 1250/5A.
Dipilih dari DESIGN AMPERE (Pact = Pt x Ku x (1 + spare)). ASUMSI - koordinasikan dengan kapasitas DEG.
6. Sel kuning (cos phi, tegangan, LOAD EQUIPMENT, Ku, spare) adalah input - boleh diubah.
7. EF D-001.09~28 SMOKE EXTRACT (ACTIVE ON EMERGENCY) + EF D-001.01~08 NORMAL, semua dengan kontaktor 24VDC
interlock ke fire alarm (FRC 1x2C-2.5mm²). Daya 15.96 kW x 1.2 = 19.152 kW/unit sesuai sheet FAN.
8. Sesuai note 12 sheet FAN: BS EN 12101-3 F400/120, motor class H, kabel tahan api, emergency overload bypass.
9. Kabel FRC 25mm² (emergency) / 16mm² (normal) per fan = ASUMSI, cek derating grouping di tray.

## CABLE SIZING
PERHITUNGAN KABEL FEEDER INCOMING - CP-FGW-L0-MVAC (GABUNGAN L0 + L1, DARI MDB-FGW-L0)
Basis: IEC 60364-5-52 (ampacity & faktor koreksi) + IEC 60364-4-43 (Ib <= In <= Iz)
DATA UMUM (sel kuning = input)
U - Tegangan line-line |  |  | V
cos phi |  |  | -
sin phi |  |  | -
Ca - faktor koreksi suhu 40C (XLPE) |  | 0.91 | -
Batas drop tegangan |  | 4% | -
PANEL | OPSI | KONFIGURASI KABEL | Ib (A) DESIGN AMPERE | In (A) | L (m) | RUN | LUAS mm² | Iz TABEL A/run | Cg | Iz TOTAL (A) | Ib<=In<=Iz ? | R90 ohm/km | X ohm/km | DROP (V) | DROP (%) | HASIL
CP-FGW-L0-MVAC | A | 2x(4C x 240mm²) Cu/XLPE/PVC + 1x(1C x 120mm²) G/Y |  | 500 | 100 | 2 | 240 | 538 | 0.88 |  |  | 0.0961 | 0.07
CP-FGW-L0-MVAC | B | 2x(4C x 185mm²) Cu/XLPE/PVC + 1x(1C x 95mm²) G/Y |  | 500 | 100 | 2 | 185 | 456 | 0.88 |  |  | 0.1247 | 0.072
CATATAN
1. Iz TABEL = IEC 60364-5-52 tabel B.52.12, Cu/XLPE 90C, 3 konduktor berbeban, 30C, metode E (multicore di tray). Konservatif; ganti dengan datasheet pabrikan (terutama kabel FRC).
2. Cg = pengelompokan run paralel bersentuhan: 1 = 1.00, 2 = 0.88, 3 = 0.82, 4 = 0.77, 5 = 0.75.
3. R90 & X = nilai tipikal Cu/XLPE multicore (ohm/km). Ganti dengan data pabrikan.
4. Drop tegangan: dV = SQRT(3) x Ib x L x (R cos phi + X sin phi) / jumlah run.
5. Panjang feeder 100 m = ASUMSI; sesuaikan dengan routing aktual.
6. Run paralel wajib identik (IEC 60364-5-52 cl.523.7). PE mengikuti IEC 60364-5-54 (S > 35mm2 -> S/2).
7. Feeder incoming panel dari MDB-FGW-L0 memakai kabel Cu/XLPE/PVC biasa; kabel tahan api (FRC) hanya untuk circuit fan smoke extract.
8. Ib = DESIGN AMPERE tiap panel (Pact = Pt x Ku x (1 + spare)), sama dengan dasar pemilihan incoming di gambar.